## Sheet1
Main Menu | Sub Menus | Details
Metering | Summary | Average current | V
|  | Average VL-L | V
|  | Power 3 phase | kW
|  | Energy net | kWh
|  | Frequency | Hz
| Current/Min/Max | L1 | A
|  | L2 | A
|  | L3 | A
|  | N | A
|  | G | A
| Current_Graph | L1 | %
|  | L2 | %
|  | L3 | %
|  | N | %
|  | G | %
| Voltage/Min/Max | L1-N | V
|  | L2-N | V
|  | L3-N | V
|  | L1-L2 | V
|  | L2-L3 | V
|  | L3-L1 | V
| Power | Real(L1/L2/L3/Total) | kW
|  | Reactive(L1/L2/L3/Total) | kVar
|  | Apparent(L1/L2/L3/Total/PowerFactor) | kVA
| Energy | Forward Active | kWh
|  | Reverse Active | kWh
|  | Net Active | kWh
|  | Total Active | kWh
|  | Leading Reactive | kVarh
|  | Lagging Reactive | kVarh
|  | Net Reactive | kVarh
|  | Total Reactive | kVarh
|  | Apparent | kVarh
| Power Demand | Real | kW
|  | Reactive | kVar
|  | Apparent | kVA
|  | Real Peak | kW
|  | Reactive Peak | kVar
|  | Apparent Peak | kVA
| Reset | Current | YES/NO
|  | L-N Voltage | YES/NO
|  | L-L Voltage | YES/NO
|  | Peak Demand | YES/NO
|  | All Max/Min | YES/NO
Events | Summary(#200) | Minor Alarm (1-13,15-51,53-56,58,60-63,65,67-70,72-76,78-85,87-99,103,108,110-113,115,117-121,123-128,130-134,136-139,141-145,147-150,162-167,171-175), Alarm (14,57,64,71,77,86,114,122,129,140,146,151-161,168,169,170), Trip no waveform (52,59,66,100,102,104-107,109,116,135,176-200) | Timestamp
| Trip(#10) | Trip Cause Trip Condition Trip Time | Ground Cause/Short Delay/ Instantaneous A Timestamp
| Alarm(#10) | Alarm Cause Alarm Condition Alarm Time | Operations Count/Setpoints error/Calibration/Configuration reading/Digital bypass trip NA Timestamp
| Time Change(#5) | Original Time New Time | Timestamp Timestamp
Diagnostics | Summary | Health Summary | %
| Short Circuit | Short Delay Instantneous High Current Total
| Overload | Phase Ground Total
| Operation | Trip Open Test Manual Total Last Operation Date Last Operation Time
| Runtime(Runtime since last reset) | Days Hours Minutes
Settings | View Settings | Long Delay | LD= ON/OFF lr(A) tr(s) HL Alarm(%) HL Warn(%)
|  | Short Delay | lsd(lr) tsd(s) Slope(Flat)
|  | Instantaneous | li(ln)
|  | Ground Fault | GF lg(l)n tg(s) Slope(Flat) Pre-alarm(%)
|  | ZSI | ON/OFF
|  | Thermal memory | Long Delay (ON/OFF) Ground Fault(ON/OFF)
|  | Neutral | %
| Protect Settings | 4 Digit pass (****)
|  | Long Delay | LD(ON/OFF) lr(MA) HL Alarm(%) HL Warn(%) LD(ON/OFF) lr(MA) HL Alarm(%) HL Warn(%)
|  | Short Delay | lsd (lr) tsd (Ms) Slope=Flat
|  | lnstantaneous | li(ln)
|  | Ground Fault | GF(Trip/Alarm/OFF) Pre-alarm(%)
|  | ZSI | ON/OFF
|  | Thermal Memory | Long Delay(ON/OFF) Ground Fault(ON/OFF)
|  | Neutral | (%)
| Unit Settings | Language | Language Selection Options
|  | Password | 4 Digit pass (***)
|  | Time(Set Time) | Set date and time
|  | Power Setup | Power Feed(Forward/Reverse) Sign Conversion(IEC/IEEE/IEEEalt) Power Window(Fixed/Sliding) Power Demand Interval(mins)
|  | Relay #1 | HW Fault Watchdog Thermal Mem Alarm-Ground Fault High temp High Load Warning Alarm-High Overload All Trips Maint Mode Trip- Ground Fault Instantaneous Short Delay Short Circuit Neutral Current Trip- High Overload Relay OFF Close Breaker Open Breaker ZSI Output ZSI Input ZSI Active ARMS Active Bell Contact Aux Contact All Faults Comms Fault 25% Health
|  | Relay #2 | HW Fault Watchdog Thermal Mem Alarm-Ground Fault High temp High Load Warning Alarm-High Overload All Trips Maint Mode Trip- Ground Fault Instantaneous Short Delay Short Circuit Neutral Current Trip- High Overload Relay OFF Close Breaker Open Breaker ZSI Output ZSI Input ZSI Active ARMS Active Bell Contact Aux Contact All Faults Comms Fault 25% Health