## Sheet1
Main menu | Metering | Events | Diagnostics | Settings | Test | Unit | Value set test
Metering | ~ Main menu | Summary | Current | Current_Graph | Voltage | Power | Energy | Power Demand | Reset
Events | ~ Main menu | Summary | Trip | Alarm | Time Change
Diagnostics | ~ Main menu | Summary | Short Circuit | Overload | Operation | Runtime | Reset
Settings | ~ Main menu | View Settings | Protect. Settings | Unit Settings
Test | ~ Main menu | Local | Remote
Unit | ~ Main menu |  | Catalog# | PXR25VLGAM | Ir | A | Firmware1# | . . | Firmware2# | . .
Summary | ~ Metering |  | Average current |  | Average VL-L |  | Power 3 phase |  | Energy net |  | Frequency
Current (A) | ~ Metering | } Max Current | L1 | L2 | L3 | N | G
Max Current (A) | ~ Current | } Min Current | L1 | L2 | L3 | N | G
Min Current (A) | ~ Max Current | { Metering | L1 | L2 | L3 | N | G
Current % | ~ Metering |  | L1/A |  | L2/B |  | L3/C
Voltage (V) | ~ Metering | } Voltage Max | L1-N | L2-N | L3-N | L1-L2 | L2-L3 | L3-L1
Voltage Max (V) | ~ Voltage | } Voltage Min | L1-N | L2-N | L3-N | L1-L2 | L2-L3 | L3-L1
Voltage Min(V) | ~ Voltage Max | { Metering | L1-N | L2-N | L3-N | L1-L2 | L2-L3 | L3-L1
Power | ~ Metering |  | Real |  | Reactive |  | Apparent |  | Power Factor
Energy | ~ Metering |  | Forward Active |  | Reverse Active |  | Net Active |  | Total Active |  | Leading Reactive | Lagging Reactive | Net Reactive | Total Reactive | Apparent
PowerDemand | ~ Metering |  | Real |  | Reactive |  | Apparent |  | Real Peak |  | Reactive Peak | Apparent Peak
Reset Max/Min | ~ Metering | Current | L-N Voltage | L-L Voltage | Peak Demand | All Max/Min | Energy
Reset Max/Min | YES | NO
Summary | ~ Events
Trip Event | ~ Events |  | Trip Cause | Trip condition | Trip Time
Alarm Event | ~ Events |  | Alarm Cause | Alarm condition | Alarm Time
Time Change | ~ Events |  | Original Time | New Time
Health Summary | ~ Diagnostics |  | Service Recomm.
ShortCircuit | ~ Diagnostics |  | Short Delay |  | Instantneous |  | High Current |  | Total
Overload | ~ Diagnostics |  | Phase |  | Ground |  | Total
Operation | ~ Diagnostics |  | Trip |  | Open |  | Test |  | Manual |  | Total | Last Operation Date | Last Operation Time
Run Time Since Last Reset | ~ Diagnostics |  | Days |  | Hours |  | Minutes
Reset | ~ Diagnostics | Trips | Operation | Runtime | All
Test | Open Breaker? | Y | N
View Settings | ~ Settings | Long Delay | Short Delay | Instantenous | Ground Fault | Thermal Memory | Neutral | ARMS mode
Long Delay | ~ ViewSettings | Ir = A | tr = Sec | Slope =
Short Delay | ~ ViewSettings | Isd = (*Ir) | tsd = Sec | Slope =
Instantneous | ~ ViewSettings | Ii = (*In)
GroundFaultOff | ~ ViewSettings | GF = OFF
GroundFaultAlarm | ~ ViewSettings | GF = | Ig = (*In) | tg = sec | Slope =
GroundFaultTrip | ~ ViewSettings | GF = Trip | Ig = 5.1(*In) | tg = 100.0 sec | Slope = Flat
ThermalMemory | ~ View Settings | Long Delay | Ground Fault
Neutral | ~ View Settings
Maintenance Mode | ~ View Settings | R = (xIn)
Protection | ~ Settings | Long Delay | Short Delay | Instantaneous | Ground Fault | Thermal Memory | Neutral | ARMS mode
Long Delay | ~ ProtectSettings | Ir = A | tr = Sec | Slope =
Short Delay | ~ ProtectSettings | Isd = (*Ir) | tsd = Sec | Slope =
Instantneous | ~ ProtectSettings | Ii = (*In )
GroundFault | ~ Protect Settings | GF | Ig = (*In) | tg = sec | Slope =
ThermalMemory | ~ Protect Settings | Long Delay | Ground Fault
Neutral | ~ ProtectSettings
Maintenance Mode | ~ Protect Settings | R = (xIn)
Unit Settings | ~ Settings | Language | Password | COM Protocols | Time | Power Feed | ZSI | High Load | Relay #1 | Relay #2
Language | ~ Unit Settings
Comms Protocols | ~ Unit Settings | Modbus Port | Ethernet Module | Profibus Module
Modbus Port | ~ COM Prot | Address | Baudrate | Parity | Stop Bit
Ethernet CAM | ~ COM Prot | DHCP | IP Address | . . . | Subnet Mask |  | Default Gateway | . | Reset Pin
Profibus CAM | ~ Comms Prot | Address
Set Time | ~ Unit Settings
ZSI | ~ Unit Settings
ZSI | ~ Unit Settings

## Sheet2
Main menu | Metering | Events | Diagnostics | Settings | Test | Unit | Summary | Current (A) | Max Current (A) | Min Current (A) | Current % | Voltage (V) | Voltage Max (V) | Voltage Min(V) | Power | Energy | PowerDemand | Reset Max/Min | Reset Max/Min | Summary | Trip Event | Alarm Event | Time Change | Health Summary | ShortCircuit | Overload | Operation | Run Time Since Last Reset | Reset | Test | View Settings | Long Delay | Short Delay | Instantneous | GroundFaultOff | GroundFaultAlarm | GroundFaultTrip | ThermalMemory | Neutral | Maintenance Mode | Protection | Long Delay | Short Delay | Instantneous | GroundFault | ThermalMemory | Neutral | Maintenance Mode | Unit Settings | Language | Comms Protocols | Modbus Port | Ethernet CAM | Profibus CAM | Set Time | ZSI | ZSI
Metering | ~ Main menu | ~ Main menu | ~ Main menu | ~ Main menu | ~ Main menu | ~ Main menu | ~ Metering | ~ Metering | ~ Current | ~ Max Current | ~ Metering | ~ Metering | ~ Voltage | ~ Voltage Max | ~ Metering | ~ Metering | ~ Metering | ~ Metering | YES | ~ Events | ~ Events | ~ Events | ~ Events | ~ Diagnostics | ~ Diagnostics | ~ Diagnostics | ~ Diagnostics | ~ Diagnostics | ~ Diagnostics | Open Breaker? | ~ Settings | ~ ViewSettings | ~ ViewSettings | ~ ViewSettings | ~ ViewSettings | ~ ViewSettings | ~ ViewSettings | ~ View Settings | ~ View Settings | ~ View Settings | ~ Settings | ~ ProtectSettings | ~ ProtectSettings | ~ ProtectSettings | ~ Protect Settings | ~ Protect Settings | ~ ProtectSettings | ~ Protect Settings | ~ Settings | ~ Unit Settings | ~ Unit Settings | ~ COM Prot | ~ COM Prot | ~ Comms Prot | ~ Unit Settings | ~ Unit Settings | ~ Unit Settings
Events | Summary | Summary | Summary | View Settings | Local |  |  | } Max Current | } Min Current | { Metering |  | } Voltage Max | } Voltage Min | { Metering |  |  |  | Current | NO | [9 empty] | Trips | Y | Long Delay | Ir = A | Isd = (*Ir) | Ii = (*In) | GF = OFF | GF = | GF = Trip | Long Delay |  | R = (xIn) | Long Delay | Ir = A | Isd = (*Ir) | Ii = (*In ) | GF | Long Delay |  | R = (xIn) | Language |  | Modbus Port | Address | DHCP | Address
Diagnostics | Current | Trip | Short Circuit | Protect. Settings | Remote | Catalog# | Average current | L1 | L1 | L1 | L1/A | L1-N | L1-N | L1-N | Real | Forward Active | Real | L-N Voltage |  |  | Trip Cause | Alarm Cause | Original Time | Service Recomm. | Short Delay | Phase | Trip | Days | Operation | N | Short Delay | tr = Sec | tsd = Sec |  |  | Ig = (*In) | Ig = 5.1(*In) | Ground Fault |  |  | Short Delay | tr = Sec | tsd = Sec |  | Ig = (*In) | Ground Fault |  |  | Password |  | Ethernet Module | Baudrate | IP Address
Settings | Current_Graph | Alarm | Overload | Unit Settings |  | PXR25VLGAM |  | L2 | L2 | L2 |  | L2-N | L2-N | L2-N |  |  |  | L-L Voltage |  |  | Trip condition | Alarm condition | New Time | [5 empty] | Runtime |  | Instantenous | Slope = | Slope = |  |  | tg = sec | tg = 100.0 sec |  |  |  | Instantaneous | Slope = | Slope = |  | tg = sec |  |  |  | COM Protocols |  | Profibus Module | Parity | . . .
Test | Voltage | Time Change | Operation |  |  | Ir | Average VL-L | L3 | L3 | L3 | L2/B | L3-N | L3-N | L3-N | Reactive | Reverse Active | Reactive | Peak Demand |  |  | Trip Time | Alarm Time |  |  | Instantneous | Ground | Open | Hours | All |  | Ground Fault |  |  |  |  | Slope = | Slope = Flat |  |  |  | Ground Fault |  |  |  | Slope = |  |  |  | Time |  |  | Stop Bit | Subnet Mask
Unit | Power |  | Runtime |  |  | A |  | N | N | N |  | L1-L2 | L1-L2 | L1-L2 |  |  |  | All Max/Min | [12 empty] | Thermal Memory | [9 empty] | Thermal Memory | [7 empty] | Power Feed
Value set test | Energy |  | Reset |  |  | Firmware1# | Power 3 phase | G | G | G | L3/C | L2-L3 | L2-L3 | L2-L3 | Apparent | Net Active | Apparent | Energy | [6 empty] | High Current | Total | Test | Minutes |  |  | Neutral | [9 empty] | Neutral | [7 empty] | ZSI |  |  |  | Default Gateway
| Power Demand |  |  |  |  | . . | [5 empty] | L3-L1 | L3-L1 | L3-L1 | [16 empty] | ARMS mode | [9 empty] | ARMS mode | [7 empty] | High Load |  |  |  | .
| Reset |  |  |  |  | Firmware2# | Energy net | [7 empty] | Power Factor | Total Active | Real Peak | [7 empty] | Total |  | Manual | [21 empty] | Relay #1 |  |  |  | Reset Pin
[6 empty] | . . | [42 empty] | Relay #2
[7 empty] | Frequency | [8 empty] | Leading Reactive | Reactive Peak | [9 empty] | Total
[16 empty] | Lagging Reactive | Apparent Peak | [9 empty] | Last Operation Date
[16 empty] | Net Reactive | [10 empty] | Last Operation Time
Total Reactive
Apparent

## Sheet3
[7 empty] | No USB tool nor IAR used | IAR | USB Tool | Adam G. -feedback, explanations
Main menu
Metering | Summary | Average current
Average VL-L
Power 3 phase
Energy net
Frequency
| Current/Min/Max | L1
L2
L3
|  | N |  |  | NeuSenorSel
|  | G |  |  | GfSel
| Current_Graph | L1/A
L2/B
L3/C
| Voltage/Min/Max | L1-N | How we will behave if N voltage sensor will not be connected?
L2-N
L3-N
L1-L2
L2-L3
L3-L1
| Power | Real | [5 empty] | real power exchange +/- sign |  | Depends on value of ReverFeed setpoint
|  | Reactive | [5 empty] | reactive power exchange +/- sign |  | Depends on value of RevFeed and SignConv setpoints
Apparent
Power Factor
| Energy | Forward Active | [5 empty] | whole energy menu can show + or - sign
Reverse Active
Net Active
Total Active
Leading Reactive
Lagging Reactive
Net Reactive
Total Reactive
Apparent
| Power Demand | Real | [5 empty] | real power demand exchange +/- sign |  | Depends on value of ReverFeed setpoint
|  | Reactive | [5 empty] | reactive power demand exchange +/- sign |  | Depends on value of RevFeed and SignConv setpoints
Apparent
Real Peak
Reactive Peak
Apparent Peak
| Reset | Current
L-N Voltage
L-L Voltage
Peak Demand
|  | All Max/Min | [5 empty] | does not reset MAX values AN,BN,CN, |  | OK, I will take a look at it
|  | Energy |  |  |  |  | ENERGY NOT IN MENU |  |  | That's OK -required by marketing
Events | Summary
Trip
Alarm
Time Change
Diagnostics | Summary | Health Summary
| Short Circuit | Short Delay
Instantneous
High Current
|  | Total |  |  |  |  | NEVER ENDING MENU |  | infinite total, number is rising with each press | Try it again with latest commit of NZM2 Please add comment with more detailed explanation of behavior (how it happens, does it happen always?)
| Overload | Phase
|  | Ground |  |  | GfSel
Total
| Operation | Trip
Open
Test
Manual
Total
Last Operation Date
Last Operation Time
| Runtime | Days
Hours
Minutes
Settings | View Settings | Long Delay | Ir = A | [5 empty] | LD in menu | To be discussed with marketing if it is OK for them
tr = Sec
Slope =
|  | Short Delay | Isd = (*Ir) |  | SdSel
|  |  | tsd = Sec |  | SdSel
|  |  | Slope = |  | SdSel
|  | Instantenous | Ii = (*In) |  |  |  | corrupted menu |  | corrupted menu | Please check again with latest commit and provide closer explanation on behavior
|  | Ground Fault | GF = On/Off |  | GfSel
|  |  | Ig = (*In) |  | GfSel
|  |  | tg = sec |  | GfSel
|  |  | Slope = |  | GfSel
|  | Thermal memory | Long Delay |  |  |  | ZSI between GF and TM |  | ZSI between GF and TM | OK, required ba marketing
Ground Fault
|  | Neutral | 0-100% |  | NeuSel
|  | ARMS mode | R??? |  | ARMSel
| Protect. Settings | Long Delay | Ir = A |  |  |  | wrong password leads to View Setting Menu |  | wrong password leads to View Setting Menu | OK, that's required by marketing
tr = Sec
|  |  | Slope = | [5 empty] | ZSI isnt supposed to be in Protection Settings | OK, that's required by marketing
|  | Short Delay | Isd = (*Ir) |  | SdSel
|  |  | tsd = Sec |  | SdSel
|  |  | Slope = |  | SdSel
|  | Instantenous | Ii = (*In)
|  | Ground Fault | GF = On/Off |  | GfSel |  | backlight of active line on just in Ground Fault Menu
|  |  | Ig = (*In) |  | GfSel
|  |  | tg = sec |  | GfSel
|  |  | Slope = |  | GfSel
|  | Thermal memory | Long Delay
Ground Fault
|  | Neutral | 0-100% |  | NeuSel |  | 60%, 100%, but 0 with no % |  | 60%, 100%, but 0 with no % | I will check if it is according to marketing spec.
|  | ARMS mode | R??? |  | ARMSel
| Unit Settings | Language | Language selection list
|  | Password | Password change?
|  | COM Protocols | Modbus Port | Address | Some flags and communication with BSM needed | ModbusSel |  |  | COMM protocols cannot be turned off | Check latest commit, should be OK there
|  |  |  | Baudrate |  | CAMSel
|  |  |  | Parity |  | IOModuleSel
Stop Bit
|  |  | Ethernet Module | DHCP
IP Address
Subnet Mask
Default Gateway
Reset Pin
|  |  | Profibus | Address
|  | Time | SetTime |  |  |  | Time save does not work |  | Time save does not work | Probably error in RTC, for display it should be OK. To be tested in future again with latest version of PXR TOOLKIT
|  | Power Feed | Forward/Reverse
|  | ZSI | ZSI On/Off? |  | ZSISel |  | ZSI not in menu…in View Seting menu ZSI = ON |  | ZSI and High load missing | OK, that's required by marketing
|  | High load | ??? |  |  |  | NOT in Menu
|  | Relay #1 | ??? |  | RelaySel |  |  |  | Relay #1,#2 - still visible | Probably missing functionality, I will check it in code
|  | Relay #2 | ??? |  | RelaySel
Test | Local | Open Breaker?
| Remote | Trip Time
| Remote | Trip Current
Unit | Catalog# | [5 empty] | Missing Catalog number |  | missing Catalog | OK, that's agreed with marketing
Ir
Firmware1#
Firmware2#
[7 empty] | Míla |  | Radek
Note on C13: Drabek, Tomas: What about graph of N, G?
Note on D66: Drabek, Tomas: Merge to one screen?
Note on E83: Drabek, Tomas: How does it work?
Note on E98: Drabek, Tomas: How does it work?
Note on C99: Drabek, Tomas: Wrong refresh of headline
Note on M115: Gabriel, Adam: Corrected in newest FW commit no.: a801fe on NZM2 repository
Note on C117: Drabek, Tomas: Wrong behavior of menu move?

## INFO
Name | Miloslav Chlad, Radomír Křečan
Creation date | 2017-10-25
Commit PXR toolkit - ID | 1153b4e
Commit PXR toolkit - Date | 2017-09-30
Commit NZM2_prot-pxr25 - ID | ba3d23d
Commit NZM2_prot-pxr25 - Date | 2017-10-25

## Updated menu structure
[6 empty] | NZM3 | NZM2 | No USB tool nor IAR used | IAR | USB Tool | Adam G. -feedback, explanations
Main menu
Metering | Summary | Average current
Average VL-L
Power 3 phase
Energy net
Frequency
| Current/Min/Max | L1
L2
L3
|  | N |  |  | NeuSenorSel | If IN and/or IG disabled the zero value is visible and misplaced (3rd row), and some dots are visible | OK
|  | G |  |  | GfSel
| Current_Graph | L1/A
L2/B
L3/C
| Voltage/Min/Max | L1-N | How we will behave if N voltage sensor will not be connected?
L2-N
L3-N
L1-L2
L2-L3
L3-L1
| Power | Real
Reactive
Apparent
Power Factor
| Energy | Forward Active
Reverse Active
Net Active
Total Active
Leading Reactive
Lagging Reactive
Net Reactive
Total Reactive
Apparent
| Power Demand | Real
Reactive
Apparent
Real Peak
Reactive Peak
Apparent Peak
| Reset | Current
L-N Voltage
L-L Voltage
Peak Demand
All Max/Min
Energy
Events | Summary
Trip
Alarm
| Time Change |  |  |  |  | Doesn't contain anything??? -> works well
Diagnostics | Summary | Health Summary
| Short Circuit | Short Delay
Instantneous
High Current
Total
| Overload | Phase
|  | Ground |  |  | GfSel
|  | Total |  |  |  | Hidden when GfSel = 0 | Not hidden when GfSel = 0
| Operation | Trip
Open
Test
Manual
Total
Last Operation Date
Last Operation Time
| Runtime | Days
Hours
Minutes
| View Settings | Long Delay | LD On/Off
Settings |  |  | Ir = A
tr = Sec
Slope =
High load alarm
High load warning
|  | Short Delay | Isd = (*Ir) |  | SdSel
|  |  | tsd = Sec |  | SdSel
|  |  | Slope = |  | SdSel
|  | Instantenous | Ii = (*In)
|  | Ground Fault | GF = On/Off |  | GfSel
|  |  | Ig = (*In) |  | GfSel
|  |  | tg = sec |  | GfSel
|  |  | Slope = |  | GfSel
|  |  | GF prealarm |  | GfSel
|  | Thermal memory | Long Delay
Ground Fault
|  | Neutral | 0-100% |  | NeuSel | NeuSel = 0 -> still visible | hidden
|  | ARMS mode | R??? |  | ARMSel | ARMSel = 0 -> Maintenance mode still visible | hidden
| Protect. Settings | Long Delay | LD On/Off
Ir = A
tr = Sec
Slope =
High load alarm
High load warning
|  | Short Delay | Isd = (*Ir) |  | SdSel
|  |  | tsd = Sec |  | SdSel
|  |  | Slope = |  | SdSel
|  | Instantenous | Ii = (*In)
|  | Ground Fault | GF = On/Off |  | GfSel
|  |  | Ig = (*In) |  | GfSel
|  |  | tg = sec |  | GfSel
|  |  | Slope = |  | GfSel
|  |  | GF prealarm |  | GfSel
|  | Thermal memory | Long Delay
Ground Fault
|  | Neutral | 0-100% |  | NeuSel | NeuSel = 0 -> can be changed between 0-60-100% | hidden
|  | ARMS mode | R??? |  | ARMSel | ARMSel = 0 -> Maintenance mode still visible and ON/OFF can be switched | hidden
| Unit Settings | Language | Language selection list |  |  | Chinese and Russian don't work | These two are not available
|  | Password | Password change?
|  | COM Protocols | Modbus Port | Address | Some flags and communication with BSM needed
Baudrate
Parity
Stop Bit
|  |  | Ethernet Module | DHCP
IP Address
Subnet Mask
Default Gateway
Reset Pin
|  |  | Profibus | Address
|  | Time | SetTime
|  | Power setup | Power Feed | Forward/Reverse
Sign Convention
Power Window
Power demand interval
|  | ZSI | ZSI On/Off? |  | ZSISel | ZSISel = 1 -> item not visible | same
|  | High load | ??? |  |  | not available | same
|  | Relay #1 | ??? |  | RelaySel | RelaySel doesn't do anything | RelaySel = 0 -> hidden
|  | Relay #2 | ??? |  | RelaySel
|  | Pole A location |  |  |  | not available | same
Test | Local | Open Breaker?
| Remote | Trip Time |  |  |  | No test -> Trip time and Trip Current visible while Hardware_Simulated_Test and Firmware_Simulated_Test set in debug mode
| Remote | Trip Current
Unit | Catalog# |  |  |  |  | not available
| Ir |  |  |  |  | Ir -> In
Firmware1#
Firmware2#
Other observations:
[6 empty] | IG missing in the screensaver when Ground is enabled | the same problem
IN visible in the screensaver when Neutral is disabled
ECAM connection:
[6 empty] | Different values in the web interface compared to the display | the same problem
No option for ECAM in the menu (not detected by the TU, the flag is not set)
The communication fails often (CAM Link status LED GREEN/RED)
Note on D66: Drabek, Tomas: Merge to one screen?
Note on C107: Drabek, Tomas: Wrong refresh of headline
Note on C129: Drabek, Tomas: Wrong behavior of menu move?