## Sheet1
function | Item | range
DisplayServices_GetProtectionThermMem | ThermMem | 0, 1
DisplayServices_GetProtectionZSI | ZSI | 0, 1
DisplayServices_GetProtectionLpickup | Lpickup | 20-250
DisplayServices_GetProtectionLtime | Ltime | sec*10 step 1
DisplayServices_GetProtectionLslope | Lslope | 0, 1, 2, 3
DisplayServices_GetProtectionL_HL_Alarm | L_HL_Alarm | 50-120 step 5
DisplayServices_GetProtectionL_HL_Warn | L_HL_Warn | 50-120 step 5
DisplayServices_GetProtectionSpickup | Spickup | pu*10 step 1
DisplayServices_GetProtectionStime | Stime | sec*1000 step 10
DisplayServices_GetProtectionSslope | Sslope | 0, 1
DisplayServices_GetProtectionIpickup | Ipickup | pu*10; 0, 20-120 step 5
DisplayServices_GetProtectionG_T_A_Off | G_T_A_Off | 0-2
DisplayServices_GetProtectionGThermMem | GThermMem | 0, 1
DisplayServices_GetProtectionGpickup | Gpickup | pu*100 step 1
DisplayServices_GetProtectionGtime | Gtime | sec*1000 step 10
DisplayServices_GetProtectionGslope | Gslope | 0, 1
DisplayServices_GetProtectionGF_Prealarm | GF_Prealarm | *100, 50-100 step 5
DisplayServices_GetProtectionNeutral | Neutral | 0, 60, 100
DisplayServices_GetProtectionARMS_Overall | ARMS_Overall | b8 0, 1
DisplayServices_GetProtectionARMS_LCD_bit | ARMS_LCD_bit | b2 0, 1
DisplayServices_GetProtectionARMS_COM_bit | ARMS_COM_bit | b0 0, 1
DisplayServices_GetProtectionARMS | ARMS | b8 0, 1
DisplayServices_GetProtectionARMS_Level | ARMS_Level | 1-5 step 1
DisplayServices_GetProtectionHighLoadWarn | HighLoadWarn | 0, 1
DisplayServices_GetProtectionHighLoadAlarm | HighLoadAlarm | 0, 1
DisplayServices_GetProtectionHighLoadSetpoint | HighLoadSetpoint | 50-120 step 5
DisplayServices_GetProtectionOverloadSetpoint | OverloadSetpoint | 50-120 step 5
DisplayServices_GetRelay1State | Relay1State | 0, 1
DisplayServices_GetRelay2State | Relay2State | 0, 1
DisplayServices_GetRelaySetpoints | RelaySetpoints | ???
DisplayServices_GetUnitLanguage | UnitLanguage | 0, 1, …. ???
DisplayServices_GetUnitPowerFeed | UnitPowerFeed | 0, 1
DisplayServices_GetUnitSignConv | UnitSignConv | 0, 1, 2
DisplayServices_GetUnitPowerDemandInterval | UnitPowerDemandInterval | 5-60 step 1
DisplayServices_GetUnitPowerWindow | UnitPowerWindow | 0, 1
DisplayServices_GetUnitRelay | UnitRelay | 0-30 ?
DisplayServices_GetUnitPoleA | UnitPoleA | 0, 1
DisplayServices_GetRegFromTime | RegFromTime | h/m/s
DisplayServices_GetTimeFromReg | TimeFromReg | h/m/s
DisplayServices_GetUnitTime | UnitTime | h/m/s
DisplayServices_GetRegFromDate | RegFromDate | y/m/d
DisplayServices_GetDateFromReg | DateFromReg | y/m/d
DisplayServices_GetUnitDate | UnitDate | y/m/d
DisplayServices_GetVoltage_L1_N | Voltage_L1_N | uint32
DisplayServices_GetVoltage_L2_N | Voltage_L2_N | uint32
DisplayServices_GetVoltage_L3_N | Voltage_L3_N | uint32
DisplayServices_GetVoltage_L1_L2 | Voltage_L1_L2 | uint32
DisplayServices_GetVoltage_L2_L3 | Voltage_L2_L3 | uint32
DisplayServices_GetVoltage_L3_L1 | Voltage_L3_L1 | uint32
DisplayServices_GetVoltage_Average | Voltage_Average | uint32
DisplayServices_GetMaxVoltage_L1_N | MaxVoltage_L1_N | uint32
DisplayServices_GetMaxVoltage_L2_N | MaxVoltage_L2_N | uint32
DisplayServices_GetMaxVoltage_L3_N | MaxVoltage_L3_N | uint32
DisplayServices_GetMaxVoltage_L1_L2 | MaxVoltage_L1_L2 | uint32
DisplayServices_GetMaxVoltage_L2_L3 | MaxVoltage_L2_L3 | uint32
DisplayServices_GetMaxVoltage_L3_L1 | MaxVoltage_L3_L1 | uint32
DisplayServices_GetMinVoltage_L1_N | MinVoltage_L1_N | uint32
DisplayServices_GetMinVoltage_L2_N | MinVoltage_L2_N | uint32
DisplayServices_GetMinVoltage_L3_N | MinVoltage_L3_N | uint32
DisplayServices_GetMinVoltage_L1_L2 | MinVoltage_L1_L2 | uint32
DisplayServices_GetMinVoltage_L2_L3 | MinVoltage_L2_L3 | uint32
DisplayServices_GetMinVoltage_L3_L1 | MinVoltage_L3_L1 | uint32
DisplayServices_GetCurrent_L1 | Current_L1 | uint32
DisplayServices_GetCurrent_L2 | Current_L2 | uint32
DisplayServices_GetCurrent_L3 | Current_L3 | uint32
DisplayServices_GetCurrent_N | Current_N | uint32
DisplayServices_GetCurrent_G | Current_G | uint32
DisplayServices_GetCurrent_Average | Current_Average | uint32
DisplayServices_GetRealPowerA | RealPowerA | int32
DisplayServices_GetRealPowerB | RealPowerB | int32
DisplayServices_GetRealPowerC | RealPowerC | int32
DisplayServices_GetRealPowerTotal | RealPowerTotal | int32
DisplayServices_GetReactivePowerA | ReactivePowerA | uint32
DisplayServices_GetReactivePowerB | ReactivePowerB | uint32
DisplayServices_GetReactivePowerC | ReactivePowerC | uint32
DisplayServices_GetReactivePowerTotal | ReactivePowerTotal | uint32
DisplayServices_GetApparentPowerA | ApparentPowerA | int32
DisplayServices_GetApparentPowerB | ApparentPowerB | int32
DisplayServices_GetApparentPowerC | ApparentPowerC | int32
DisplayServices_GetApparentPowerTotal | ApparentPowerTotal | int32
DisplayServices_GetPowerFactor | PowerFactor | int32
DisplayServices_GetActiveEnergyFwd | ActiveEnergyFwd | int32 positive
DisplayServices_GetActiveEnergyRev | ActiveEnergyRev | int32 positive
DisplayServices_GetActiveEnergyTotal | ActiveEnergyTotal | int32 positive
DisplayServices_GetActiveEnergyNet | ActiveEnergyNet | int32
DisplayServices_GetReactiveEnergyLead | ReactiveEnergyLead | int32 positive
DisplayServices_GetReactiveEnergyLagging | ReactiveEnergyLagging | int32 positive
DisplayServices_GetReactiveEnergyTotal | ReactiveEnergyTotal | int32
DisplayServices_GetReactiveEnergyNet | ReactiveEnergyNet | int32
DisplayServices_GetApparentEnergyNet | ApparentEnergyNet | int32
DisplayServices_GetRealPowerDemand | RealPowerDemand | int32
DisplayServices_GetReactivePowerDemand | ReactivePowerDemand | int32
DisplayServices_GetApparentPowerDemand | ApparentPowerDemand | int32
DisplayServices_GetRealPeakPowerDemand | RealPeakPowerDemand | int32
DisplayServices_GetReactivePeakPowerDemand | ReactivePeakPowerDemand | int32
DisplayServices_GetApparentPeakPowerDemand | ApparentPeakPowerDemand | int32
DisplayServices_GetFrequency | Frequency | uint32
DisplayServices_GetMaxCurrent_L1 | MaxCurrent_L1 | uint32
DisplayServices_GetMaxCurrent_L2 | MaxCurrent_L2 | uint32
DisplayServices_GetMaxCurrent_L3 | MaxCurrent_L3 | uint32
DisplayServices_GetMaxCurrent_N | MaxCurrent_N | uint32
DisplayServices_GetMaxCurrent_G | MaxCurrent_G | uint32
DisplayServices_GetMinCurrent_L1 | MinCurrent_L1 | uint32
DisplayServices_GetMinCurrent_L2 | MinCurrent_L2 | uint32
DisplayServices_GetMinCurrent_L3 | MinCurrent_L3 | uint32
DisplayServices_GetMinCurrent_N | MinCurrent_N | uint32
DisplayServices_GetMinCurrent_G | MinCurrent_G | uint32
DisplayServices_GetMinIr | MinIr | 88-252, step 1
DisplayServices_GetMaxIr | MaxIr | 220-630, step1
DisplayServices_GetMintr | Mintr | 20
DisplayServices_GetMaxtr | Maxtr | 140, 200
DisplayServices_GetMinIsd | MinIsd | 15, 20
DisplayServices_GetMaxIsd | MaxIsd | 70, 100
DisplayServices_GetMintsd_I2t | Mintsd_I2t | 0
DisplayServices_GetMaxtsd_I2t | Maxtsd_I2t | 1000
DisplayServices_GetMintsd_Flat | Mintsd_Flat | 0
DisplayServices_GetMaxtsd_Flat | Maxtsd_Flat | 1000
DisplayServices_GetMinIi | MinIi | 20
DisplayServices_GetMaxIi | MaxIi | 80, 120, 150, 180
DisplayServices_GetMinIg | MinIg | 20
DisplayServices_GetMaxIg | MaxIg | 100
DisplayServices_GetMintg_I2t | Mintg_I2t | 0
DisplayServices_GetMaxtg_I2t | Maxtg_I2t | 1000
DisplayServices_GetMintg_Flat | Mintg_Flat | 0
DisplayServices_GetMaxtg_Flat | Maxtg_Flat | 1000
DisplayServices_GetUnitPassword | UnitPassword | uint16 (9999)
DisplayServices_GetUnitModbusAddress | UnitModbusAddress | uint16
DisplayServices_GetUnitModbusBaudRate | UnitModbusBaudRate | uint16
DisplayServices_GetUnitModbusParity | UnitModbusParity | uint16
DisplayServices_GetUnitModbusStopBit | UnitModbusStopBit | uint16
DisplayServices_GetUnitEthernetDHCP_Enable | UnitEthernetDHCP_Enable | uint16
DisplayServices_GetUnitEthernetAddress_MSB | UnitEthernetAddress_MSB | uint16
DisplayServices_GetUnitEthernetAddress_2 | UnitEthernetAddress_2 | uint16
DisplayServices_GetUnitEthernetAddress_3 | UnitEthernetAddress_3 | uint16
DisplayServices_GetUnitEthernetAddress_LSB | UnitEthernetAddress_LSB | uint16
DisplayServices_GetUnitEthernet_Subnet_Mask | UnitEthernet_Subnet_Mask | uint16
DisplayServices_GetUnitEthernetDefault_Gateway1 | UnitEthernetDefault_Gateway1 | uint16
DisplayServices_GetUnitEthernetDefault_Gateway2 | UnitEthernetDefault_Gateway2 | uint16
DisplayServices_GetUnitEthernetReset_Pin | UnitEthernetReset_Pin | uint16
DisplayServices_GetUnitProfibusAddress | UnitProfibusAddress | uint16
DisplayServices_GetSC_SDTripCntr | SC_SDTripCntr | uint16
DisplayServices_GetSC_InstTripCntr | SC_InstTripCntr | uint16
DisplayServices_GetSC_HighCurrentTripCntr | SC_HighCurrentTripCntr | uint16
DisplayServices_GetTotalSCCntr | TotalSCCntr | uint16
DisplayServices_GetLDTripCntr | LDTripCntr | uint16
DisplayServices_GetGFTripCntr | GFTripCntr | uint16
DisplayServices_GetLifePoint | LifePoint | uint16
DisplayServices_GetTotalOverloadCntr | TotalOverloadCntr | uint16
DisplayServices_GetTripOpCntr | TripOpCntr | uint16
DisplayServices_GetOpenOpCntr | OpenOpCntr | uint16
DisplayServices_GetTestOpCntr | TestOpCntr | uint16
DisplayServices_GetManualOpCntr | ManualOpCntr | uint16
DisplayServices_GetTotalOpCntr | TotalOpCntr | uint16
DisplayServices_GetDiagLastOperDate | DiagLastOperDate | y/m/d
DisplayServices_GetDiagLastOperTime | DiagLastOperTime | h/m/s
DisplayServices_GetRunningDay | RunningDay | uint16
DisplayServices_GetRunningHour | RunningHour | uint16
DisplayServices_GetRunningMin | RunningMin | uint16
DisplayServices_GetUnitFW_Version | UnitFW_Version | struct ???
DisplayServices_GetFactory1 | Factory1 | bit struct ???
DisplayServicesGetMODBUS_Sel | MODBUS | 0,1
DisplayServicesGetCAM_Sel | CAM | 0,1
DisplayServicesGetCAM_Status | CAM_Status | 0,3,4
DisplayServicesGetSD_Sel | SD | 0,1
DisplayServicesGetInst_Sel | Inst | 0,1
DisplayServicesGetNeuSensorSel | NeuSensorSel | 0,1
DisplayServicesGetGF_Sel | GF | 0,1
DisplayServicesGetThermal_Sel | Thermal | 0,1
DisplayServicesGetARMS_Sel | ARMS | 0,1
DisplayServicesGetZSI_Sel | ZSI | 0,1
DisplayServicesGetRelay_Sel | Relay | 0,1
DisplayServicesGetBreakerRating | BreakerRating | uint16